## 1. Contents
Workbook Contents
Click on tabs at the bottom of the screen to access the following:
Tab 1. Contents (current tab)
Tab 2. Head Loss/Frictional Pressure Drop
Tab 3. Pipe Flow Rate
Tab 4. Required Diameter
Why you shouldn’t give copies of this workbook away
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy
the spreadsheet you purchased. We have deliberately set our prices so low that no one
can really claim that they can’t afford to pay. But low prices will work for us—that is, we
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be
available for you in the future.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Copyright © 2011 Harlan H. Bengtson. All Rights Reserved.

## 2. head loss
Pipe Flow/Friction Factor Calculations I: (U.S. units)
Calculation of Head Loss, hL, and Frictional Pressure Drop, DPf, | [7 empty] | Moody Friction Factor Equations
for given flow rate, Q, pipe diam., D, pipe length, L,
pipe roughness, e, and fluid properties, r & m.
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
1. Determine Friction Factor, f, assuming completely turbulent flow {f = [1.14 + 2 log10(D/e)]-2}
Inputs (enter values in the blue boxes) |  |  |  |  | Calculations (done by spreadsheet)
Pipe Diameter, Din = |  | 6 | in |  | Pipe Diameter, D = | 0.5 | ft
Pipe Roughness, e = |  | 0.0005 | ft |  | Friction Factor, f = | 0.019616
Pipe Length, L = |  | 100 | ft |  | Cross-Sect. Area, A = | 0.19635 | ft2 |  | Pipe Roughness Values
Pipe Flow Rate, Q = |  | 0.6 | cfs |  | Ave. Velocity, V = | 3.0558 | ft/sec
Fluid Density, r = |  | 1.94 | slugs/ft3 |  | Reynolds number, Re = | 108575.1524
Fluid Viscosity, m = |  | 2.73e-05 | lb-sec/ft2
2. Check on whether the given flow is "completely turbulent flow"
(Calculate f with the transition region equation and see if differs from the one calculated above.)
f = {-2*log10[((e/D)/3.7)+(2.51/(Re*(f1/2))]}-2
Transition Region Friction Factor, f: |  |  |  | f = | 0.022129
Repeat calc of f using new value of f: |  |  |  | f = | 0.022001
Repeat again if necessary: |  |  |  | f = | 0.022007
3. Calculate hL and DPf, using the final value for f calculated in step 2
Equations: hL = f(L/D)(V2/2g) and DPf = rghL
Frictional Head Loss, hL = |  | 0.63878 | ft
Frictional Pressure
Drop, DPf = |  | 39.8663 | psf
Frictional Pressure
Drop, DPf = |  | 0.27685 | psi
Copyright © 2010 Harlan H. Bengtson. All Rights Reserved.

## 3. flow rate
Pipe Flow/Friction Factor Calculations II: (U.S. units)
Calculation of Fluid Flow Rate, Q, for given frictional head loss, hL, pipe | [7 empty] | Moody Friction Factor Equations
diam., D, pipe length, L, pipe roughness, e, and fluid properties, r & m.
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
1. Determine Friction Factor, f, assuming completely turbulent flow {f = [1.14 + 2 log10(D/e)]-2}
Inputs (enter values in the blue boxes) |  |  |  |  | Calculations
Pipe Diameter, Din = |  | 4 | in |  | Pipe Diameter, D = | 0.33333 | ft
Pipe Roughness, e = |  | 0.0005 | ft |  | Friction Factor, f = | 0.021704
Pipe Length, L = |  | 40 | ft |  | Cross-Sect. Area, A = | 0.087266 | ft2
Allowable Head Loss, hL = |  | 0.9 | ft |  | Assumed Flow Rate, Q = | 0.83 | cfs
Pipe Roughness Values
Fluid Density, r = |  | 1.94 | slugs/ft3 |  | Ave. Velocity, V = | 9.5111 | ft/sec
Fluid Viscosity, m = |  | 2.73e-05 | lb-sec/ft2 |  | Reynolds number, Re = | 225293.4412
2. Check on whether the given flow is "completely turbulent flow"
(Calculate f with the transition region equation and see if differs from the one calculated above.)
f = {-2*log10[((e/D)/3.7)+(2.51/(Re*(f1/2))]}-2
Transition Region Friction Factor, f: |  |  |  | f = | 0.022711
Repeat calc of f using new value of f: |  |  |  | f = | 0.02269
Repeat again if necessary: |  |  |  | f = | 0.02269
3. Calculate V and Q, using the final value for f calculated in step 2 in the Darcy Weisbach equation
[V = (2g*D*hL/f*L)1/2 ] and Q = V(pD2/4)
Fluid Velocity, V = |  | 4.6138 | ft/sec
Fluid Flow Rate, Q = |  | 0.40263 | cfs
NOTE: This is an iterative calculation, because an assumed value of Q is used to start the
calculations. If the final calculated value of Q is different from the assumed value, then the
assumed value of Q should be replaced with the calculated value of Q, leading to a new
calculated value for Q. This should be repeated as many times as necessary to get the
calculated value for Q to be the same as the assumed value. This iteration typically converges
rather rapidly.
This spreadsheet shows only the final assumed and calculated values of Q (when they are equal).
If the initial assumed value of Q was 1.5 cfs, then subsequent calculated and assumed values
for Q, leading to the final solution are as follows:
|  | Assumed Q, cfs |  |  | Calculated Q, cfs
|  | 1.5 |  |  | 0.85
|  | 0.85 |  |  | 0.83
|  | 0.83 |  |  | 0.83
Copyright © 2010 Harlan H. Bengtson. All Rights Reserved.

## 4. diameter
Pipe Flow/Friction Factor Calculations III: ( U.S. units )
Calculation of pipe diameter, D, for given flow rate, Q, pipe length, L, | [8 empty] | Moody Friction Factor Equations
pipe roughness, e, head loss, hL, and fluid properties, r & m.
(NOTE: This is an iterative calculation. An initial assumed value of D will be used.)
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
1. Determine Friction Factor, f, assuming completely turbulent flow {f = [1.14 + 2 log10(D/e)]-2}
Inputs |  |  |  |  | Calculations
Allowable Head Loss, hL = |  | 20 | ft |  | Assumed Pipe Diam, Din* = |  | 4 | in
Pipe Roughness, e = |  | 0.0005 | ft |  | Pipe Diameter, D = |  | 0.33333 | ft
Pipe Length, L = |  | 100 | ft |  | Friction Factor, f = |  | 0.021704 |  | Pipe Roughness Values
Pipe Flow Rate, Q = |  | 0.6 | cfs |  | Cross-Sect. Area, A = |  | 0.087266 | ft2
Fluid Density, r = |  | 1.94 | slugs/ft3 |  | Ave. Velocity, V = |  | 6.8755 | ft/sec
Fluid Viscosity, m = |  | 2.7e-05 | lb-sec/ft2 |  | Reynolds number, Re = |  | 164672.3145
2. Check on whether the given flow is "completely turbulent flow"
(Calculate f with the transition region equation and see if differs from the one calculated above.)
[ f = {-2*log10[((e/D)/3.7)+(2.51/(Re*(f1/2))]}-2 ]
Transistion Region Friction Factor, f: |  |  |  | f = | 0.023049
Repeat calc of f using new value of f: |  |  |  | f = | 0.023012
Repeat again if necessary: |  |  |  | f = | 0.023013
3. Calculate pipe diameter, D using the final value for f calculated in step 2
[ D = f(L/hL)(V2/2g) ]
Pipe Diameter, D = |  | 0.084543 | ft | = | 1.0145 | in
NOTE: This iterative procedure doesn't converge smoothly to a solution. If the calculated pipe diameter
in this step is larger than the assumed pipe diameter above, then replace the assumed pipe diameter
value with the next larger standard pipe size. Repeat until you find the smallest standard pipe diameter
that gives a smaller calculated required pipe diameter. That is your solution.
With the example values given here, an assumed pipe diameter of 3 inches gives a calculated pipe
diameter requirement of 3.4 inches, increasing the assumed pipe diameter to the next standard pipe size
( 3.5 inches ) gives a calculated pipe diameter requirement of 1.8 inches, so a 3.5 inch size is the
minimum standard pipe diameter that will do the job.
*Standard nominal U.S. pipe sizes in inches:
1/8, 1/4, 3/8, 1/2, 3/4, 1, 1 1/4, 1 1/2, 2, 2 1/2, 3, 3 1/2, 4, 5, 6, 8, 10, 12, 14, 16, 18, 20, 24,
30, 42, 48, 54, 60
Copyright © 2010 Harlan H. Bengtson. All Rights Reserved.